## Asset Schedule Intro
Asset Schedule Data Requirements
Asset Schedule Data Requirements | All maintainable assets should be defined as separate line items in the appropriate MEP schedule. Each asset requires the following fields: (1) Schedule Tag - see below the 'Schedule Tag Methodology'. Refer to the 'Asset Keywords & Schedule Tags' sheet for abbreviations. (2) Location - the location/room where the asset/equipment is physically installed. This field must reference the official room/location number as approved by Caltech. (3) Location Served - the location/room that the asset/equipment serves. This field must reference the official room/location number as approved by Caltech unless mutiple rooms are served. In this case, refer to floor/suite/lab, etc. (4) Served By - if the asset/equipment is served by another asset (e.g. VAV is served by the AHU), then refer to the schedule tag of the parent asset here.
Schedule Tag Methodology | The convention for creating schedule tags shown below should be used across all project plans, drawings, submittals, BAS controller object, Niagara point folders, etc. Refer to the 'Asset Schedule Tag' sheet for actual schedule tag abbreviations. Schedule Tag Abbrreviation - Floor# - Unique Sequential Number For example: AHU-R-1, AHU-R-2, AHU-B2-1, VVS-B2-1, VVS-B2-2, VVS-B1-1, VVS-B1-1 The 'Unique Sequential Number' is unique only within a given building-floor and schedule tag abbreviation combination. Floor #s are generally: B2,B1,1,2,3,4,R (roof), P (penthouse)
Using the Keyword Library | Asset Keywords & Schedule Tags is a library that lists maintainable equipment keywords and their corresponding schedule tags, QR coding requirements and attribute data requirements. Construction teams are responsible for non-internal keywords (marked as Caltech Internal = false). The list is maintained by Caltech Asset Management. Contact assets@caltech.edu for more information.

## Asset Keywords & Schedule Tags
Asset Major Group Description | Asset Group Description | Keyword Name | Schedule Tag Example | QR Sticker | Caltech Internal | As-Built Attributes List
Site Products | [23-11 00 00] SITE PRODUCTS (SERIALIZED) | GROUNDS EQUIPMENT | GRNDS-1-1 | None | true
Site Products | [23-11 00 00] SITE PRODUCTS (SERIALIZED) | GROUNDS SYSTEM | GRNDS SYS-1 | None | true
Site Products | [23-11 00 00] SITE PRODUCTS (SERIALIZED) | IRRIGATION SYSTEM | IRR SYS-1-1 | None | true
Site Products | [23-11 00 00] SITE PRODUCTS (SERIALIZED) | OUTDOOR SPACE | OUT-1-1 | None | true
Site Products | [23-11 00 00] SITE PRODUCTS (SERIALIZED) | PARKING AND PATHWAYS SYSTEM | PRKG SYS-1-1 | None | true
Site Products | [23-11 00 00] SITE PRODUCTS (SERIALIZED) | PAY STATION | PAYS-1-1 | Vinyl Sticker | false
Structural and Interior Enclosure Products | [23-13 00 00] STRUCTURAL AND EXTERIOR ENCLOSURE PRODUCTS (SYSTEM) | BUILDING EXTERIOR SYSTEM | BE SYS-1 | None | true | Composition, Install Date, Condition, Last Update, Estimated Replacement Date, Estimated Coat Date
Structural and Interior Enclosure Products | [23-13 00 00] STRUCTURAL AND EXTERIOR ENCLOSURE PRODUCTS (SYSTEM) | ROOFING AND COMPONENTS SYSTEM | ROOF SYS-1-1 | None | true | Composition, Install Date, Condition, Last Update, Estimated Replacement Date, Estimated Coat Date
Interior and Finish Products | [23-15 00 00] INTERIOR AND FINISH PRODUCTS (SYSTEM) | BUILDING INTERIOR SYSTEM | BI SYS-1 | None | true
Interior and Finish Products | [23-15 00 00] INTERIOR AND FINISH PRODUCTS (SYSTEM) | CEILING SYSTEM | CIEL SYS-1-1 | None | true
Interior and Finish Products | [23-15 00 00] INTERIOR AND FINISH PRODUCTS (SYSTEM) | FLOORING SYSTEM | FLR SYS-1-1 | None | true
Openings, Passages, and Protection Products | [23-17 00 00] OPENINGS, PASSAGES, AND PROTECTION PRODUCTS (SERIALIZED) | INTERIOR DOOR SYSTEM | DR SYS-1-1 | None | true
Openings, Passages, and Protection Products | [23-17 00 00] OPENINGS, PASSAGES, AND PROTECTION PRODUCTS (SERIALIZED) | MAINTENANCE DOOR SYSTEM | MNT DR-1-1 | None | true
Openings, Passages, and Protection Products | [23-17 00 00] OPENINGS, PASSAGES, AND PROTECTION PRODUCTS (SERIALIZED) | SPECIALTY DOORS | SPLT DR-1-1 | None | false
Openings, Passages, and Protection Products | [23-17 00 00] OPENINGS, PASSAGES, AND PROTECTION PRODUCTS (SERIALIZED) | WINDOW SYSTEM | WND SYS-1-1 | None | true
Specialty Products | [23-19 00 00] SPECIALTY PRODUCTS (PROPERTY) | BUILDING | BLDG-1-1 | None | true
Specialty Products | [23-19 00 00] SPECIALTY PRODUCTS (PROPERTY) | COMMON AREA SYSTEM | COMNX-1-1 | None | true
Specialty Products | [23-19 00 00] SPECIALTY PRODUCTS (PROPERTY) | RESTROOM SYSTEM | REST SYS-1-1 | None | true
Furnishings, Fixtures and Equipment Products | [23-21 00 00] FURNISHINGS, FIXTURES AND EQUIPMENT PRODUCTS (SERIALIZED) | CARPENTRY EQUIPMENT | CARP-1-1 | None | true
Furnishings, Fixtures and Equipment Products | [23-21 00 01] KITCHEN EQUIPMENT (SERIALIZED) | AIR CURTAIN | CURT-1-1 | Vinyl Sticker | false
Furnishings, Fixtures and Equipment Products | [23-21 00 01] KITCHEN EQUIPMENT (SERIALIZED) | CHARBOILER | CHAR-1-1 | None | true
Furnishings, Fixtures and Equipment Products | [23-21 00 01] KITCHEN EQUIPMENT (SERIALIZED) | DISHWASHER | DWSH-1-1 | None | true
Furnishings, Fixtures and Equipment Products | [23-21 00 01] KITCHEN EQUIPMENT (SERIALIZED) | DUMP STATION | DUMP-1-1 | None | true
Furnishings, Fixtures and Equipment Products | [23-21 00 01] KITCHEN EQUIPMENT (SERIALIZED) | FRYER | FRY-1-1 | None | true
Furnishings, Fixtures and Equipment Products | [23-21 00 01] KITCHEN EQUIPMENT (SERIALIZED) | GRIDDLE | GRID-1-1 | None | true
Furnishings, Fixtures and Equipment Products | [23-21 00 01] KITCHEN EQUIPMENT (SERIALIZED) | HOT HOLDING CABINET | HHLD-1-1 | None | true
Furnishings, Fixtures and Equipment Products | [23-21 00 01] KITCHEN EQUIPMENT (SERIALIZED) | ICE MACHINE | ICE-1-1 | None | false
Furnishings, Fixtures and Equipment Products | [23-21 00 01] KITCHEN EQUIPMENT (SERIALIZED) | KITCHEN EXHAUST HOOD | KH-1-1 | None | true
Furnishings, Fixtures and Equipment Products | [23-21 00 01] KITCHEN EQUIPMENT (SERIALIZED) | KITCHEN HOOD CONTROL PANEL | KHCP-1-1 | None | true
Furnishings, Fixtures and Equipment Products | [23-21 00 01] KITCHEN EQUIPMENT (SERIALIZED) | KITCHEN VENTILATION DUCT | KVENT-1-1 | None | true
Furnishings, Fixtures and Equipment Products | [23-21 00 01] KITCHEN EQUIPMENT (SERIALIZED) | OVEN | OVEN-1-1 | None | true
Furnishings, Fixtures and Equipment Products | [23-21 00 01] KITCHEN EQUIPMENT (SERIALIZED) | REFRIGERATOR | RFRG-1-1 | None | true
Furnishings, Fixtures and Equipment Products | [23-21 00 01] KITCHEN EQUIPMENT (SERIALIZED) | REMOTE PULL STATION | PULL-1-1 | None | true
Furnishings, Fixtures and Equipment Products | [23-21 00 01] KITCHEN EQUIPMENT (SERIALIZED) | SOFT SERVE | SOFT-1-1 | None | true
Conveying Systems and Material Handling Products | [23-23 00 01] CONVEYING SYSTEMS - ELEVATOR (SERIALIZED) | DUMBWAITER | DUM-1-1 | Metal Dogtag | false | Funded Fiscal Year, Rating, Capacity, Type, In Service Date, Project Number
Conveying Systems and Material Handling Products | [23-23 00 01] CONVEYING SYSTEMS - ELEVATOR (SERIALIZED) | ELEVATOR | ELEV-1-1 | Metal Dogtag | false | Funded Fiscal Year, Rating, Capacity, Type, In Service Date, Project Number
Conveying Systems and Material Handling Products | [23-23 00 01] CONVEYING SYSTEMS - ELEVATOR (SERIALIZED) | HANDICAP LIFT | HANDI-1-1 | Metal Dogtag | false | Funded Fiscal Year, Rating, Capacity, Type, In Service Date, Project Number
Medical and Laboratory Equipment | [23-25 00 00] MEDICAL AND LABORATORY EQUIPMENT (DURABLE) | DEWAR | DEW-1-1 | Vinyl Sticker | false | Type, Size, Manufacture Date, Dewar ID, Tare Weight
Medical and Laboratory Equipment | [23-25 00 00] MEDICAL AND LABORATORY EQUIPMENT (DURABLE) | FUME HOOD CABINET | FH-B1-1 | Vinyl Sticker | false | Type, Size, Manufacture Date, Dewar ID, Tare Weight
Medical and Laboratory Equipment | [23-25 00 00] MEDICAL AND LABORATORY EQUIPMENT (DURABLE) | FUME HOOD CANOPY | FHC-B1-1 | None | false | Type, Size, Manufacture Date, Dewar ID, Tare Weight
Medical and Laboratory Equipment | [23-25 00 01] MEDICAL AND LABORATORY EQUIPMENT - AUTOCLAVE (SERIALIZED) | AUTOCLAVE | AU-B1-1 | Vinyl Sticker | false
General Facility Services Products | [23-27 00 00] GENERAL FACILITY SERVICES PRODUCTS (SERIALIZED) | FIRE PANEL | FPNL-1-1 | None | false
General Facility Services Products | [23-27 00 00] GENERAL FACILITY SERVICES PRODUCTS (SERIALIZED) | FIRE SPRINKLER SYSTEM | SPRNK-1-1 | None | true
General Facility Services Products | [23-27 00 00] GENERAL FACILITY SERVICES PRODUCTS (SERIALIZED) | FIRE SUPPRESSION SYSTEM | FSUPR-1-1 | None | true
General Facility Services Products | [23-27 00 01] GENERAL FACILITY SERVICES PRODUCTS - MOTOR (COMPONENT) | FAN MOTOR | FMTR-B1-1 | Vinyl Sticker | false | HP, FLA, Belt Quantity, RLA, Belt Size, Frame, Voltage Phase Hertz
General Facility Services Products | [23-27 00 01] GENERAL FACILITY SERVICES PRODUCTS - MOTOR (COMPONENT) | MOTOR | MTR-1-1 | Vinyl Sticker | false | HP, FLA, Belt Quantity, RLA, Belt Size, Frame, Voltage Phase Hertz
General Facility Services Products | [23-27 00 01] GENERAL FACILITY SERVICES PRODUCTS - MOTOR (COMPONENT) | PUMP MOTOR | PMTR-B1-1 | Vinyl Sticker | false | HP, FLA, Belt Quantity, RLA, Belt Size, Frame, Voltage Phase Hertz
Facility and Occupant Protection Products | [23-29 00 00] FACILITY AND OCCUPANT PROTECTION PRODUCTS (SYSTEM) | BLOODBORNE PATHOGEN KIT | BBP-1-1 | Vinyl Sticker | false
Facility and Occupant Protection Products | [23-29 00 00] FACILITY AND OCCUPANT PROTECTION PRODUCTS (SYSTEM) | BUILDING SECURITY SYSTEM | BSCR SYS-1 | None | true
Facility and Occupant Protection Products | [23-29 00 00] FACILITY AND OCCUPANT PROTECTION PRODUCTS (SYSTEM) | EMERGENCY EXIT AND LIGHT SYSTEM | EMG LTG SYS-1-1 | None | true
Facility and Occupant Protection Products | [23-29 00 00] FACILITY AND OCCUPANT PROTECTION PRODUCTS (SYSTEM) | EMERGENCY PHONE | EMG PH-1-1 | Vinyl Sticker | false
Facility and Occupant Protection Products | [23-29 00 00] FACILITY AND OCCUPANT PROTECTION PRODUCTS (SYSTEM) | FIRE SYSTEM | FIRE SYS-1-1 | None | true
Facility and Occupant Protection Products | [23-29 00 00] FACILITY AND OCCUPANT PROTECTION PRODUCTS (SYSTEM) | PORTABLE AED AND FIRE EXTINGUISHER SYSTEM | FEXT SYS-1-1 | None | true
Facility and Occupant Protection Products | [23-29 00 00] FACILITY AND OCCUPANT PROTECTION PRODUCTS (SYSTEM) | SAFETY HARNESS | HARN-1-1 | Metal Dogtag | false
Facility and Occupant Protection Products | [23-29 00 01] FACILITY AND OCCUPANT PROTECTION - AED (SERIALIZED) | AED | AED-1-1 | Vinyl Sticker | false | Battery, Child Pads, Adult Pads
Facility and Occupant Protection Products | [23-29 00 02] FACILITY AND OCCUPANT PRODUCTS - CARD READER DOOR (SERIALIZED) | CARD READER DOOR | CRDR-1-1 | None | true | Control Panel Type
Facility and Occupant Protection Products | [23-29 00 03] FACILITY AND OCCUPANT PROTECTION - FIRE EXTINGUISHERS (SERIALIZED) | FIRE EXTINGUISHER | FEXT-1-1 | Vinyl Sticker | false | Type, Capacity, Manufacture Hydrostatic Date
Plumbing Specific Products and Equipment | [23-31 00 00] PLUMBING SPECIFIC PRODUCTS AND EQUIPMENT (COMPONENT) | CONDENSATE RECOVERY SYSTEM | CND RSYS-1-1 | Vinyl Sticker | false
Plumbing Specific Products and Equipment | [23-31 00 00] PLUMBING SPECIFIC PRODUCTS AND EQUIPMENT (COMPONENT) | DHW SYSTEM | DHW SYS-1-1 | None | true
Plumbing Specific Products and Equipment | [23-31 00 00] PLUMBING SPECIFIC PRODUCTS AND EQUIPMENT (COMPONENT) | EMERGENCY WASH | EMG WSH-1-1 | Vinyl Sticker | false
Plumbing Specific Products and Equipment | [23-31 00 00] PLUMBING SPECIFIC PRODUCTS AND EQUIPMENT (COMPONENT) | EMERGENCY WASH SYSTEM | EWASH-1-1 | None | true
Plumbing Specific Products and Equipment | [23-31 00 00] PLUMBING SPECIFIC PRODUCTS AND EQUIPMENT (COMPONENT) | HHW SYSTEM | HHW SYS-1-1 | None | true
Plumbing Specific Products and Equipment | [23-31 00 00] PLUMBING SPECIFIC PRODUCTS AND EQUIPMENT (COMPONENT) | HYDRATION STATION | WS-1-1 | Vinyl Sticker | false
Plumbing Specific Products and Equipment | [23-31 00 00] PLUMBING SPECIFIC PRODUCTS AND EQUIPMENT (COMPONENT) | OIL INTERCEPTOR | INTC-1-1 | None | false
Plumbing Specific Products and Equipment | [23-31 00 00] PLUMBING SPECIFIC PRODUCTS AND EQUIPMENT (COMPONENT) | PLUMBING SYSTEM | PLB SYS-1-1 | None | true
Plumbing Specific Products and Equipment | [23-31 00 00] PLUMBING SPECIFIC PRODUCTS AND EQUIPMENT (COMPONENT) | SOFTENER | SFTR-1-1 | Vinyl Sticker | false
Plumbing Specific Products and Equipment | [23-31 00 01] PLUMBING - HEAT EXCHANGER (SERIALIZED) | CHILLED WATER HEAT EXCHANGER | HX-B1-1 | Vinyl Sticker | false | System Served, Connection Size, Capacity GAL, Service, HS Entering Water Temp, CS Entering Water Temp, CS Leaving Water Temp, Supply Flow, Precharge Pressure, Type, Equipment Served, Capacity MBH, Pressure Rating, HS Leaving Water Temp
Plumbing Specific Products and Equipment | [23-31 00 01] PLUMBING - HEAT EXCHANGER (SERIALIZED) | DOMESTIC HOT WATER HEAT EXCHANGER | HX-1-1 | Vinyl Sticker | false | System Served, Connection Size, Capacity GAL, Service, HS Entering Water Temp, CS Entering Water Temp, CS Leaving Water Temp, Supply Flow, Precharge Pressure, Type, Equipment Served, Capacity MBH, Pressure Rating, HS Leaving Water Temp
Plumbing Specific Products and Equipment | [23-31 00 01] PLUMBING - HEAT EXCHANGER (SERIALIZED) | HEATING HOT WATER HEAT EXCHANGER | HX-B1-1 | Vinyl Sticker | false | System Served, Connection Size, Capacity GAL, Service, HS Entering Water Temp, CS Entering Water Temp, CS Leaving Water Temp, Supply Flow, Precharge Pressure, Type, Equipment Served, Capacity MBH, Pressure Rating, HS Leaving Water Temp
Plumbing Specific Products and Equipment | [23-31 00 01] PLUMBING - HEAT EXCHANGER (SERIALIZED) | PROCESS CHILLED WATER HEAT EXCHANGER | HX-B1-1 | Vinyl Sticker | false | System Served, Connection Size, Capacity GAL, Service, HS Entering Water Temp, CS Entering Water Temp, CS Leaving Water Temp, Supply Flow, Precharge Pressure, Type, Equipment Served, Capacity MBH, Pressure Rating, HS Leaving Water Temp
Plumbing Specific Products and Equipment | [23-31 00 02] PLUMBING - AIR SEPARATOR (SERIALIZED) | AIR SEPARATOR | ASPR-1-1 | None | false | Connection Size
Plumbing Specific Products and Equipment | [23-31 00 03] PLUMBING - TANK (SERIALIZED) | AIR PRESSURE TANK | APTK-1-1 | Vinyl Sticker | false | Capacity, Precharge Pressure, System Served
Plumbing Specific Products and Equipment | [23-31 00 03] PLUMBING - TANK (SERIALIZED) | AIR TANK | ATK-1-1 | Vinyl Sticker | false | Capacity, Precharge Pressure, System Served
Plumbing Specific Products and Equipment | [23-31 00 03] PLUMBING - TANK (SERIALIZED) | BRINE WATER TANK | BWTK-1-1 | Vinyl Sticker | false | Capacity, Precharge Pressure, System Served
Plumbing Specific Products and Equipment | [23-31 00 03] PLUMBING - TANK (SERIALIZED) | EXPANSION TANK | ET-1-1 | Vinyl Sticker | false | Capacity, Precharge Pressure, System Served
Plumbing Specific Products and Equipment | [23-31 00 03] PLUMBING - TANK (SERIALIZED) | FUEL TANK | FTANK-1-1 | Vinyl Sticker | false | Capacity, Precharge Pressure, System Served
Plumbing Specific Products and Equipment | [23-31 00 03] PLUMBING - TANK (SERIALIZED) | WATER TANK | WTNK-1-1 | Vinyl Sticker | false | Capacity, Precharge Pressure, System Served
Plumbing Specific Products and Equipment | [23-31 00 04] PLUMBING - PUMP (COMPONENT) | CHILLED WATER PUMP | CHWP-B1-1 | Vinyl Sticker | false | Basin Size, Equipment Served, HP, Operating Temp, Service, Inlet Size, RPM, Type, Design Flow Rate, Discharge Nominal Diameter, Identification, Voltage Phase Hertz, Total Design Head, Impeller Size, Discharge Size, Suction Nominal Diameter
Plumbing Specific Products and Equipment | [23-31 00 04] PLUMBING - PUMP (COMPONENT) | CONDENSER WATER PUMP | CWP-B1-1 | Vinyl Sticker | false | Basin Size, Equipment Served, HP, Operating Temp, Service, Inlet Size, RPM, Type, Design Flow Rate, Discharge Nominal Diameter, Identification, Voltage Phase Hertz, Total Design Head, Impeller Size, Discharge Size, Suction Nominal Diameter
Plumbing Specific Products and Equipment | [23-31 00 04] PLUMBING - PUMP (COMPONENT) | DOMESTIC HOT WATER PUMP | DHWP-B1-1 | Vinyl Sticker | false | Basin Size, Equipment Served, HP, Operating Temp, Service, Inlet Size, RPM, Type, Design Flow Rate, Discharge Nominal Diameter, Identification, Voltage Phase Hertz, Total Design Head, Impeller Size, Discharge Size, Suction Nominal Diameter
Plumbing Specific Products and Equipment | [23-31 00 04] PLUMBING - PUMP (COMPONENT) | HEATING HOT WATER PUMP | HHWP-B1-1 | Vinyl Sticker | false | Basin Size, Equipment Served, HP, Operating Temp, Service, Inlet Size, RPM, Type, Design Flow Rate, Discharge Nominal Diameter, Identification, Voltage Phase Hertz, Total Design Head, Impeller Size, Discharge Size, Suction Nominal Diameter
Plumbing Specific Products and Equipment | [23-31 00 04] PLUMBING - PUMP (COMPONENT) | INDUSTRIAL COLD WATER PUMP | ICWP-B1-1 | Vinyl Sticker | false | Basin Size, Equipment Served, HP, Operating Temp, Service, Inlet Size, RPM, Type, Design Flow Rate, Discharge Nominal Diameter, Identification, Voltage Phase Hertz, Total Design Head, Impeller Size, Discharge Size, Suction Nominal Diameter
Plumbing Specific Products and Equipment | [23-31 00 04] PLUMBING - PUMP (COMPONENT) | INDUSTRIAL HOT WATER PUMP | IHWP-B1-1 | Vinyl Sticker | false | Basin Size, Equipment Served, HP, Operating Temp, Service, Inlet Size, RPM, Type, Design Flow Rate, Discharge Nominal Diameter, Identification, Voltage Phase Hertz, Total Design Head, Impeller Size, Discharge Size, Suction Nominal Diameter
Plumbing Specific Products and Equipment | [23-31 00 05] PLUMBING - WATER HEATER (SERIALIZED) | ELECTRIC WATER HEATER | EWH-1 | Vinyl Sticker | false | Type, Capacity, Storage Capacity, Recovery Capacity, Service, Outlet Water Supply Temp, KW, Voltage Phase Hertz
Plumbing Specific Products and Equipment | [23-31 00 05] PLUMBING - WATER HEATER (SERIALIZED) | GAS WATER HEATER | GWH-1-1 | Vinyl Sticker | false | Type, Capacity, Storage Capacity, Recovery Capacity, Service, Outlet Water Supply Temp, KW, Voltage Phase Hertz
Plumbing Specific Products and Equipment | [23-31 00 05] PLUMBING - WATER HEATER (SERIALIZED) | STEAM WATER HEATER | STMH-1-1 | Vinyl Sticker | false | Type, Capacity, Storage Capacity, Recovery Capacity, Service, Outlet Water Supply Temp, KW, Voltage Phase Hertz
Plumbing Specific Products and Equipment | [23-31 00 06] PLUMBING - BACKFLOW PREVENTER (SERIALIZED) | BACKFLOW PREVENTER | BFP-1-1 | Metal Dogtag | false | Commissioning Initial Test Company, Connection Size, Commissioning Initial Test Tester Number, Commissioning Initial Test Date, Orientation, Type of Protection, Other Water Usage, Water Usage, Assembly Type
Plumbing Specific Products and Equipment | [23-31 00 07] PLUMBING - FILTER (SERIALIZED) | WATER FILTER | FLT-R-1 | Vinyl Sticker | false | Type
HVAC Specific Products and Equipment | [23-33 00 00] HVAC SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | ACTIVE BEAM | AB-1-1 | None | false
HVAC Specific Products and Equipment | [23-33 00 00] HVAC SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | AIR DRYER | DRYR-1-1 | Metal Dogtag | false
HVAC Specific Products and Equipment | [23-33 00 00] HVAC SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | AIR RECEIVER | ARVR-1-1 | Metal Dogtag | false
HVAC Specific Products and Equipment | [23-33 00 00] HVAC SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | AIRCUITY SYSTEM | ACTY SYS-1-1 | None | false
HVAC Specific Products and Equipment | [23-33 00 00] HVAC SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | EXHAUST FAN SYSTEM | EAF SYS-B1-1 | None | true
HVAC Specific Products and Equipment | [23-33 00 00] HVAC SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | HVAC SYSTEM | HVAC SYS-1 | None | true
HVAC Specific Products and Equipment | [23-33 00 00] HVAC SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | HVAC TESTING SYSTEM | TEST SYS-1 | None | true
HVAC Specific Products and Equipment | [23-33 00 00] HVAC SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | LAB EXHAUST FAN SYSTEM | EAF SYS-B1-1 | None | true
HVAC Specific Products and Equipment | [23-33 00 01] HVAC - AIR HANDLER (SERIALIZED) | AIR HANDLER | AHU-R-1 | Vinyl Sticker | false | Cooling Type, CFM, UV Lights, 100% Outside Air, Flow Measuring Station, Supply Fan Drive Type, Heating Type, Magnahelic, VFD
HVAC Specific Products and Equipment | [23-33 00 01] HVAC - AIR HANDLER (SERIALIZED) | PACKAGED AIR HANDLER UNIT | PAHU-1-1 | Vinyl Sticker | false | Cooling Type, CFM, UV Lights, 100% Outside Air, Flow Measuring Station, Supply Fan Drive Type, Heating Type, Magnahelic, VFD
HVAC Specific Products and Equipment | [23-33 00 02] HVAC - FILTER (SERIALIZED) | FILTER BANK | FLTB-1-1 | Vinyl Sticker | false | Quantity 3, Type, Type 3, Size, Rating, Size 4, Quantity 4, Size 3, Quantity 2, Size 2, Type 2, Type 4, Rating 4, Quantity, Rating 2, Rating
HVAC Specific Products and Equipment | [23-33 00 02] HVAC - FILTER (SERIALIZED) | ZONE DIFFUSER FILTER | FLTB-1-1 | Vinyl Sticker | false | Quantity 3, Type, Type 3, Size, Rating, Size 4, Quantity 4, Size 3, Quantity 2, Size 2, Type 2, Type 4, Rating 4, Quantity, Rating 2, Rating
HVAC Specific Products and Equipment | [23-33 00 03] HVAC - FAN (COMPONENT) | EXHAUST FAN | EF-R-1 | Vinyl Sticker | false | Drive Type, Air System Type, CFM, Bearing, Belt Size, Shop Number
HVAC Specific Products and Equipment | [23-33 00 03] HVAC - FAN (COMPONENT) | LAB EXHAUST FAN | EAF-1-1 | Vinyl Sticker | false | Drive Type, Air System Type, CFM, Bearing, Belt Size, Shop Number
HVAC Specific Products and Equipment | [23-33 00 03] HVAC - FAN (COMPONENT) | RETURN FAN | RAF-R-1 | None | false | Drive Type, Air System Type, CFM, Bearing, Belt Size, Shop Number
HVAC Specific Products and Equipment | [23-33 00 03] HVAC - FAN (COMPONENT) | SUPPLY FAN | SAF-B1-1 | None | false | Drive Type, Air System Type, CFM, Bearing, Belt Size, Shop Number
HVAC Specific Products and Equipment | [23-33 00 04] HVAC - AIR COMPRESSOR (SERIALIZED) | AIR COMPRESSOR | ACMPR-1-1 | Vinyl Sticker | false | Horsepower, Cooling, Voltage Phase Hertz, Pressure, Type, Stages
HVAC Specific Products and Equipment | [23-33 00 06] HVAC - HUMIDIFIER (SERIALIZED) | HUMIDIFIER | HUM-B1-1 | Vinyl Sticker | false
HVAC Specific Products and Equipment | [23-33 00 07] HVAC - TERMINAL VAV BOX (SERIALIZED) | CAV EXHAUST BOX | CVE-B1-1 | Vinyl Sticker | false | Min Air Flow, Max Air Flow, Inlet Diameter, Max Air Velocity, Reheat Type
HVAC Specific Products and Equipment | [23-33 00 07] HVAC - TERMINAL VAV BOX (SERIALIZED) | CAV RETURN BOX | CVR-B1-1 | Vinyl Sticker | false | Min Air Flow, Max Air Flow, Inlet Diameter, Max Air Velocity, Reheat Type
HVAC Specific Products and Equipment | [23-33 00 07] HVAC - TERMINAL VAV BOX (SERIALIZED) | CAV SUPPLY BOX | CVS-B1-1 | Vinyl Sticker | false | Min Air Flow, Max Air Flow, Inlet Diameter, Max Air Velocity, Reheat Type
HVAC Specific Products and Equipment | [23-33 00 07] HVAC - TERMINAL VAV BOX (SERIALIZED) | VAV EXHAUST BOX | VVE-B1-1 | Vinyl Sticker | false | Min Air Flow, Max Air Flow, Inlet Diameter, Max Air Velocity, Reheat Type
HVAC Specific Products and Equipment | [23-33 00 07] HVAC - TERMINAL VAV BOX (SERIALIZED) | VAV RETURN BOX | VVR-B1-1 | Vinyl Sticker | false | Min Air Flow, Max Air Flow, Inlet Diameter, Max Air Velocity, Reheat Type
HVAC Specific Products and Equipment | [23-33 00 07] HVAC - TERMINAL VAV BOX (SERIALIZED) | VAV SUPPLY BOX | VVS-B1-1 | Vinyl Sticker | false | Min Air Flow, Max Air Flow, Inlet Diameter, Max Air Velocity, Reheat Type
HVAC Specific Products and Equipment | [23-33 00 08] HVAC - TERMINAL AIR VALVE (SERIALIZED) | LAB FUMEHOOD EXHAUST AIR VALVE | EAV-B1-1 | None | false | Reheat Type, Min Air Flow, Inlet Diameter, Max Air Flow
HVAC Specific Products and Equipment | [23-33 00 08] HVAC - TERMINAL AIR VALVE (SERIALIZED) | LAB GENERAL EXHAUST AIR VALVE | GEV-B1-1 | None | false | Reheat Type, Min Air Flow, Inlet Diameter, Max Air Flow
HVAC Specific Products and Equipment | [23-33 00 08] HVAC - TERMINAL AIR VALVE (SERIALIZED) | LAB RETURN AIR VALVE | RAV-B1-1 | None | false | Reheat Type, Min Air Flow, Inlet Diameter, Max Air Flow
HVAC Specific Products and Equipment | [23-33 00 08] HVAC - TERMINAL AIR VALVE (SERIALIZED) | LAB SUPPLY AIR VALVE | SAV-B1-1 | None | false | Reheat Type, Min Air Flow, Inlet Diameter, Max Air Flow
HVAC Specific Products and Equipment | [23-33 00 09] HVAC - CONTROL DAMPER (SERIALIZED) | DUCT BRANCH CONTROL DAMPER | CD-R-1 | None | false | Max Face Velocity, Type
HVAC Specific Products and Equipment | [23-33 00 09] HVAC - CONTROL DAMPER (SERIALIZED) | EXHAUST AIR DAMPER | EAD-R-1 | None | false | Max Face Velocity, Type
HVAC Specific Products and Equipment | [23-33 00 09] HVAC - CONTROL DAMPER (SERIALIZED) | OUTSIDE AIR DAMPER | OAD-R-1 | None | false | Max Face Velocity, Type
HVAC Specific Products and Equipment | [23-33 00 09] HVAC - CONTROL DAMPER (SERIALIZED) | RETURN AIR DAMPER | RAD-1 | None | false | Max Face Velocity, Type
HVAC Specific Products and Equipment | [23-33 00 09] HVAC - CONTROL DAMPER (SERIALIZED) | TRANSFER AIR DAMPER | TAD-1 | None | false | Max Face Velocity, Type
HVAC Specific Products and Equipment | [23-33 00 10] HVAC - CONDENSING UNIT (SERIALIZED) | COLD ROOM CONDENSER | CNDR-1-1 | Vinyl Sticker | false | Condenser Entering Air Wet Bulb Temp, Qty Compressors, Compressor Voltage Phase Hertz, Fan Motor Horsepower, Condenser Enetering Air Dry Bulb Temp, Fan Motor Voltage Phase Hertz, Compressor Motor HP, Qty Fan Motors, Type
HVAC Specific Products and Equipment | [23-33 00 10] HVAC - CONDENSING UNIT (SERIALIZED) | CONDENSING UNIT | CDU-R-1 | Vinyl Sticker | false | Condenser Entering Air Wet Bulb Temp, Qty Compressors, Compressor Voltage Phase Hertz, Fan Motor Horsepower, Condenser Enetering Air Dry Bulb Temp, Fan Motor Voltage Phase Hertz, Compressor Motor HP, Qty Fan Motors, Type
HVAC Specific Products and Equipment | [23-33 00 10] HVAC - CONDENSING UNIT (SERIALIZED) | SPLIT SYSTEM CONDENSER | COND-1-1 | Vinyl Sticker | false | Condenser Entering Air Wet Bulb Temp, Qty Compressors, Compressor Voltage Phase Hertz, Fan Motor Horsepower, Condenser Enetering Air Dry Bulb Temp, Fan Motor Voltage Phase Hertz, Compressor Motor HP, Qty Fan Motors, Type
HVAC Specific Products and Equipment | [23-33 00 11] HVAC - EVAPORATOR FAN COIL (SERIALIZED) | COLD ROOM EVAPORATOR FAN COIL | EVAP FC-1 | Vinyl Sticker | false | Qty Fan Motors, Fan Motor V/Ph/Hz, Fan Motor HP, Tonnage
HVAC Specific Products and Equipment | [23-33 00 12] HVAC - PACKAGED AIR CONDITIONER (SERIALIZED) | PACKAGED AIR CONDITIONER | PAC-R-1 | Vinyl Sticker | false
HVAC Specific Products and Equipment | [23-33 00 14] HVAC - REFRIGERATION SYSTEM (SERIALIZED) | COLD ROOM SYSTEM | COLDRM SYS-1-1 | Vinyl Sticker | false | Refrigerant, Type
HVAC Specific Products and Equipment | [23-33 00 14] HVAC - REFRIGERATION SYSTEM (SERIALIZED) | SPLIT SYSTEM REFRIGERATION | AC-1-1 | None | false | Refrigerant, Type
HVAC Specific Products and Equipment | [23-33 00 15] HVAC CONTROLS - THERMOSTAT (SERIALIZED) | THERMOSTAT | TSTAT-B1-1 | Vinyl Sticker | false | co2 Sensor, Occupancy Sensor
HVAC Specific Products and Equipment | [23-33 00 16] HVAC - BOILER (SERIALIZED) | BOILER | BLR-B1-1 | Vinyl Sticker | false | Output, Fuel, Type, Input, Media
HVAC Specific Products and Equipment | [23-33 00 17] HVAC - CHILLER (SERIALIZED) | CHILLER | CH-B1-1 | Vinyl Sticker | false | Compressor Motor HP, Voltage Phase Hertz, Condesner Leaving Water Temp, Condenser Enetering Water Temp, Evaporator Entering Water Temp, Evaporator Flow, Refrigerant, Evaporator Leaving Water Temp
HVAC Specific Products and Equipment | [23-33 00 18] HVAC - COOLING TOWER (SERIALIZED) | COOLING TOWER | CT-R-1 | None | false
HVAC Specific Products and Equipment | [23-33 00 19] HVAC - HYDRONIC COIL (SERIALIZED) | CHILLED WATER COIL | CHWC-B1-1 | None | false
HVAC Specific Products and Equipment | [23-33 00 19] HVAC - HYDRONIC COIL (SERIALIZED) | HEATING HOT WATER COIL | HHWC-B1-1 | None | false
HVAC Specific Products and Equipment | [23-33 00 20] HVAC - CONTROL VALVE (SERIALIZED) | CHW CONTROL VALVE | CV-1-1 | None | false | Type
HVAC Specific Products and Equipment | [23-33 00 20] HVAC - CONTROL VALVE (SERIALIZED) | DHW CONTROL VALVE | CV-1-1 | None | false | Type
HVAC Specific Products and Equipment | [23-33 00 20] HVAC - CONTROL VALVE (SERIALIZED) | HHW CONTROL VALVE | CV-1-1 | None | false | Type
HVAC Specific Products and Equipment | [23-33 00 20] HVAC - CONTROL VALVE (SERIALIZED) | STEAM CONTROL VALVE | CV-1-1 | None | false | Type
HVAC Specific Products and Equipment | [23-33 00 21] HVAC - FAN COIL UNIT (SERIALIZED) | BLOWER COIL UNIT | BCU-B1-1 | Vinyl Sticker | false | Filter 1 Size, Filter 1 Type, Filter 1 Qty, Filter 2 Size, Filter 2 Type, Filter 2 Qty, Filter 1 Rating, Motor FLA, Motor RLA, Filter 2 Rating, Motor Belt Size, Motor Belt Qty, Motor HP, Motor Voltage/Phase/Hertz, Motor Frame, Motor Model, Motor Manufacturer, Flow Measuring Station
HVAC Specific Products and Equipment | [23-33 00 21] HVAC - FAN COIL UNIT (SERIALIZED) | FAN COIL UNIT | FCU-B1-1 | Vinyl Sticker | false | Filter 1 Size, Filter 1 Type, Filter 1 Qty, Filter 2 Size, Filter 2 Type, Filter 2 Qty, Filter 1 Rating, Motor FLA, Motor RLA, Filter 2 Rating, Motor Belt Size, Motor Belt Qty, Motor HP, Motor Voltage/Phase/Hertz, Motor Frame, Motor Model, Motor Manufacturer, Flow Measuring Station
HVAC Specific Products and Equipment | [23-33 00 21] HVAC - FAN COIL UNIT (SERIALIZED) | FAN FILTER UNIT | FFU-B1-1 | Vinyl Sticker | false | Filter 1 Size, Filter 1 Type, Filter 1 Qty, Filter 2 Size, Filter 2 Type, Filter 2 Qty, Filter 1 Rating, Motor FLA, Motor RLA, Filter 2 Rating, Motor Belt Size, Motor Belt Qty, Motor HP, Motor Voltage/Phase/Hertz, Motor Frame, Motor Model, Motor Manufacturer, Flow Measuring Station
HVAC Specific Products and Equipment | [23-33 00 22] HVAC CONTROLS - NIAGARA JACE (SERIALIZED) | NIAGARA JACE | JACE-CN Bldg Code-1 | Vinyl Sticker | false | SYSTEM NAME, VERSION, IP ADDRESS
HVAC Specific Products and Equipment | [23-33 00 23] HVAC CONTROLS - METERING (SERIALIZED) | BTU METER, CHW | BTU-CHW-14-B1-1 | Metal Dogtag | false
HVAC Specific Products and Equipment | [23-33 00 23] HVAC CONTROLS - METERING (SERIALIZED) | BTU METER, DHW | BTU-DHW-14-B1-1 | Metal Dogtag | false
HVAC Specific Products and Equipment | [23-33 00 23] HVAC CONTROLS - METERING (SERIALIZED) | BTU METER, HHW | BTU-HHW-14-B1-1 | Metal Dogtag | false
HVAC Specific Products and Equipment | [23-33 00 23] HVAC CONTROLS - METERING (SERIALIZED) | ELECTRIC METER | EM-14-B1-1 | Metal Dogtag | false
HVAC Specific Products and Equipment | [23-33 00 23] HVAC CONTROLS - METERING (SERIALIZED) | GAS METER, NATURAL GAS | GM-CH4-28-B1-1 | Metal Dogtag | false
HVAC Specific Products and Equipment | [23-33 00 23] HVAC CONTROLS - METERING (SERIALIZED) | GAS METER, NITROGEN | GM-N2-85-B1-1 | Metal Dogtag | false
HVAC Specific Products and Equipment | [23-33 00 23] HVAC CONTROLS - METERING (SERIALIZED) | WATER METER | WM-28-B1-1 | Metal Dogtag | false
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | CIRCUIT BREAKER | CRB-1-1 | Vinyl Sticker | false
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | CIRCUIT BREAKER | CRB-1-1 | Vinyl Sticker | false
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | DATA SYSTEM | DATA-1-1 | None | true
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | DC POWER CONTROL SYSTEM | DC SYS-1-1 | Vinyl Sticker | true
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | DISTRIBUTION BOARD | DISTP-1-1 | Vinyl Sticker | false
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | ELECTRICAL DISTRIBUTION SYSTEM | DIST SYS-1-1 | None | true
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | EMERGENCY CIRCUIT | EMG CR-1-1 | None | true
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | EMERGENCY EXIT | EMG EX-1-1 | Vinyl Sticker | false
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | EMERGENCY LIGHT | EMG LTG-1-1 | Vinyl Sticker | false
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | EMERGENCY LIGHT AND EXIT SIGN COMBO | EGR-1-1 | Vinyl Sticker | false
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | EXTERIOR LIGHTING SYSTEM | EXLTG SYS-1 | None | true
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | FUEL CELL | FCELL-1-1 | Vinyl Sticker | false
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | FUSED DISCONNECT | DISC-1-1 | Vinyl Sticker | true
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | INTERIOR LIGHTING SYSTEM | INTLTG SYS-1-1 | None | true
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | LIGHTING CONTROLS | LTGC-1-1 | None | false
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | LIGHTING INVERTER | INV-1-1 | Vinyl Sticker | false
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | LOW VOLTAGE DISCONNECT | LVD-1-1 | Vinyl Sticker | true
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | MEDIUM VOLTAGE DISCONNECT | MVD-1-1 | Vinyl Sticker | true
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | MEDIUM VOLTAGE FEEDER | TAP-1-1 | Vinyl Sticker | false
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | MEDIUM VOLTAGE SPLICE BOX | SPL-1-1 | Vinyl Sticker | true
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | MOTOR CONTROL CENTER | MCC-1-1 | Vinyl Sticker | false
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | STARTER | STRTR-1-1 | Vinyl Sticker | true
Electrical and Lighting Specific Products and Equipment | [23-35 00 00] ELECTRICAL AND LIGHTING SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | SWITCH | SW-1-1 | Vinyl Sticker | false
Electrical and Lighting Specific Products and Equipment | [23-35 00 01] ELECTRICAL - VFD (COMPONENT) | VARIABLE FREQUENCY DRIVE | VFD-B1-1 | Vinyl Sticker | false | Amperes, Voltage, Phase, Manufacture Date, HP, Power Factor
Electrical and Lighting Specific Products and Equipment | [23-35 00 02] ELECTRICAL - ELECTRICAL PANEL (COMPONENT) | PANELBOARD | PB-1-1 | Vinyl Sticker | false | Voltage, Amperes, KAIC, Emergency, Phase, Manufacture Date
Electrical and Lighting Specific Products and Equipment | [23-35 00 03] ELECTRICAL - TRANSFORMER (SERIALIZED) | TRANSFORMER | TF-1-1 | Vinyl Sticker | false | Primary Voltage, Fuse Size, Secondary Voltage, Phase , Manufacture Date, Fuse Type, Impedance, Oil Type, KVA Rating
Electrical and Lighting Specific Products and Equipment | [23-35 00 04] ELECTRICAL - GENERATOR (SERIALIZED) | GENERATOR | GEN-1-1 | Metal Dogtag | false | Permit Number, Amperes, Manufacture Date, Monitored, KVA Rating, Runtime, Phase, Output Voltage, Rated Power Output, Fuel Consumption, Fuel Type, Fuel Tank Capacity, Number of ATS
Electrical and Lighting Specific Products and Equipment | [23-35 00 05] ELECTRICAL - AUTOMATIC TRANSFER SWITCH (SERIALIZED) | AUTOMATIC TRANSFER SWITCH | ATS-1-1 | Vinyl Sticker | false | Volts, Manufacture Date, Phase, Amperes
Information and Communication Specific Products and Equipment | [23-37 00 00] INFORMATION AND COMMUNICATION SPECIFIC PRODUCTS AND EQUIPMENT (SYSTEM) | BUILDING CONTROLS SYSTEM | BAS-1 | None | true
Utility and Transportation Products | [23-39 00 00] UTILITY AND TRANSPORTATION PRODUCTS (SYSTEM) | BUILDING UTILITY SYSTEM | BUTL SYS-1 | None | true
Utility and Transportation Products | [23-39 00 00] UTILITY AND TRANSPORTATION PRODUCTS (SYSTEM) | CHEMICAL CONTROLLER | CHEMX-1-1 | Vinyl Sticker | false
Utility and Transportation Products | [23-39 00 00] UTILITY AND TRANSPORTATION PRODUCTS (SYSTEM) | CHILLED WATER SYSTEM | CHW SYS-B1-1 | None | true
Utility and Transportation Products | [23-39 00 00] UTILITY AND TRANSPORTATION PRODUCTS (SYSTEM) | CLEAN STEAM GENERATOR | STMGEN-B1-1 | Vinyl Sticker | false
Utility and Transportation Products | [23-39 00 00] UTILITY AND TRANSPORTATION PRODUCTS (SYSTEM) | CO-GEN SYSTEM | COGEN-1-1 | None | false
Utility and Transportation Products | [23-39 00 00] UTILITY AND TRANSPORTATION PRODUCTS (SYSTEM) | COMPRESSED AIR SYSTEM | CMPR ASYS-1-1 | None | true
Utility and Transportation Products | [23-39 00 00] UTILITY AND TRANSPORTATION PRODUCTS (SYSTEM) | CONDENSATE RECEIVER | CND RCR-1-1 | Vinyl Sticker | false
Utility and Transportation Products | [23-39 00 00] UTILITY AND TRANSPORTATION PRODUCTS (SYSTEM) | CONDENSER WATER SYSTEM | CDW SYS-1-1 | None | true
Utility and Transportation Products | [23-39 00 00] UTILITY AND TRANSPORTATION PRODUCTS (SYSTEM) | CONTINUOUS EMISSIONS MONITORING SYSTEM | EMSS SYS-1-1 | None | false
Utility and Transportation Products | [23-39 00 00] UTILITY AND TRANSPORTATION PRODUCTS (SYSTEM) | DEAERATOR | DAR-1-1 | Metal Dogtag | false
Utility and Transportation Products | [23-39 00 00] UTILITY AND TRANSPORTATION PRODUCTS (SYSTEM) | DEIONIZED WATER UNIT | DIWU-1-1 | Metal Dogtag | false
Utility and Transportation Products | [23-39 00 00] UTILITY AND TRANSPORTATION PRODUCTS (SYSTEM) | POT FEEDER | POT-B1-1 | Metal Dogtag | false
Utility and Transportation Products | [23-39 00 00] UTILITY AND TRANSPORTATION PRODUCTS (SYSTEM) | POWER GENERATION SYSTEM | PGEN SYS-1-1 | None | true
Utility and Transportation Products | [23-39 00 00] UTILITY AND TRANSPORTATION PRODUCTS (SYSTEM) | REDUCTION GEAR | RDGR-1-1 | Metal Dogtag | false
Utility and Transportation Products | [23-39 00 00] UTILITY AND TRANSPORTATION PRODUCTS (SYSTEM) | REVERSE OSMOSIS UNIT | ROU-1-1 | Metal Dogtag | false
Utility and Transportation Products | [23-39 00 00] UTILITY AND TRANSPORTATION PRODUCTS (SYSTEM) | STEAM SYSTEM | STM SYS-1-1 | None | true
Utility and Transportation Products | [23-39 00 00] UTILITY AND TRANSPORTATION PRODUCTS (SYSTEM) | UTILITY PLANT COMPONENT EQUIPMENT | UTIL SYS-1-1 | None | true
Utility and Transportation Products | [23-39 00 00] UTILITY AND TRANSPORTATION PRODUCTS (SYSTEM) | VACUUM PUMP | VAC-1 | Vinyl Sticker | false
Utility and Transportation Products | [23-39 00 00] UTILITY AND TRANSPORTATION PRODUCTS (SYSTEM) | VEHICLE | CAR-1-1 | Metal Dogtag | false
Utility and Transportation Products | [23-39 00 00] UTILITY AND TRANSPORTATION PRODUCTS (SYSTEM) | WATER CHEMISTRY SYSTEM | WCHM SYS-1-1 | None | true
Utility and Transportation Products | [23-39 00 00] UTILITY AND TRANSPORTATION PRODUCTS (SYSTEM) | WATER TREATMENT SYSTEM | WTRT SYS-1-1 | None | true